TECHNICAL DATA SHEET

THERMO-FLEX™

Self-Limiting Self-Regulating Heating Cable (SLSR)

### 1. Product Overview

THERMO-FLEX Heating Cable is engineered for reliable freeze protection and process temperature maintenance. Its PTC/FEP core automatically adjusts heat output relative to surface temperature, ensuring energy savings and safe operation.

## 2. Electrical Specifications

| ## Parameter | ## Specification |
| --- | --- |
| ## Rated Voltage | ## 220–230 V AC |
| ## Output Power @ 10°C | ## 25 W/m |
| ## Maximum Circuit Length | ## 100 m |

## 3. Construction Detail

| Component | Material / Specification |
| --- | --- |
| Bus Wires | Tinned Copper, 7 × 0.4mm |
| Heating Core | PTC Self-Regulating Conductor |
| Primary Insulation | Polyolefin |
| Metallic Shield | Al-Mg Alloy Braid |
| Outer Jacket | Polyolefin |
| Cable Dimensions | 9.8 mm × 4.9 mm (W × H) |
| Bending radius |  |

## 4. Temperature Ratings

| Parameter | Value |
| --- | --- |
| Minimum Installation Temperature | −40°C |
| Maximum Tolerance Temperature | 105°C |
| Maximum Maintain Temperature | 65°C |

## 5. Key Features

- Self-regulating technology: prevents overheating

- Energy-efficient power adjustment

- Cut-to-length flexibility during installation

- Durable moisture-resistant jacket

- Rugged Al-Mg metallic shield for enhanced grounding

- Suitable for harsh environments

## 6. Applications

- Industrial & commercial pipe freeze protection

- Temperature maintenance systems

- Roof/gutter de-icing

- Pipe, Tank and vessel heating

- Fire protection & sprinkler lines

## 7. Ordering Information

| Model | Voltage | Output Power | Jacket | Maximum Length |
| --- | --- | --- | --- | --- |
| THERMO-FLEX 25W | 220–230 V | 25 W/m | Polyolefin | 100 m |

## 8. Safety & Compliance

- Designed for harsh outdoor and industrial environments

- Compatible with standard circuit protection devices

- Follow installation guidelines and electrical standards

| S.NO. | Descriptions | Techno-Therm |
| --- | --- | --- |
| 1 | Maximum exposure Temp. | 105℃ |
| 2 | Maximum operating Temp. | 65℃ |
| 3 | Nominal voltage at 10.c | 25W/m |
| 4 | Min bending radius | 24.5mm(5 times Cable thickness) |
| 5 | Min Installation Temp. | -40℃ |
| 6 | Bus wires | Tinned copper, 7x0.4mm |
| 7 | Power output | 25W/m |
| 8 | Model | 25LTH2-CR |
| 9 | Insulation | Polyolefin |
| 10 | Maximum Length | 100M |